## Slide 1
Design of steel structures
under the aspect
of fire protection measures
TU BRAUNSCHWEIG
iBMB
Dr.-Ing. E. Richter
Institute for Building Materials, Concrete Structures and Fire Protection
Technical University of Braunschweig

## Slide 2: Contents
Introduction
Fire exposure
  Standard fire, natural fire
Properties of steel in fire
Protective materials
Steel temperature
  Protected and unprotected steelwork
Simple calculation model
  Critical temperature, Eurocode 3 Part 1-2
Conclusions

## Slide 3: Introduction
General objectives of fire design
  Load-carrying capacity:
    members in a structural assembly should resist the applied loads in a fire
  Insulation:
    limitation of temperature of 140 K (average) or 180 K (peak) on the unexposed side of a wall or floor
  Integrity
    limitation of breaks or cracks to avoid passage of smoke or flame to the unexposed side of a wall or floor

## Slide 4: Standard temperature/time curve
0 30 60 90 120 150 180
time [min]
1200
1000
800
600
400
200
0
temperature [°C]

## Slide 5: Natural fire - Design curves
Fully developed compartment fire
Fire load density
Opening factor
= 0.12 m1/2

## Slide 6: Steel temperature development
 Unprotected steelwork
a,t = · hnet,d · t
Am/V
ca·a
Am/V section factor [1/m]
Am exposed surface area per unit length [m2]
V volume per unit length [m3]
ca specific heat of steel [J/kgK]
a density of steel [kg/m3]
hnet,d design value of the heat flux per unit area [W/m2]
t time intervall [  5s ]
·
·

## Slide 7: Section factor Am/V
Open section
exposed to
fire on all sides
Am perimeter
V cross-section area
=
Tube exposed
to fire on all sides
Open section
exposed to
fire on three sides
 Am/V for unprotected steel members
Am 1
V t
=
Am surface exposed to fire
V cross-section area
=
Flat bar
exposed to fire
on all sides
Am 2·(b + t)
V b·t
=

## Slide 8: Steel temperature
time [min]
temperature [°C]
ISO 834
Am/V  small
Am/V  large

## Slide 9: Unprotected steel column
Damage after fire exposure
Buckling length: lfi  0.5 L
Buckling length lfi  0.7 L

## Slide 10: Structural steel
Thermal elongation
Example (beam):
l = 5 m, a = 600 °C: l  1.4*10-5*(600 - 20)*500 = 4.1 cm

## Slide 11: Unprotected steel construction
External steel frame

## Slide 12: Fire protective materials
Traditional materials ( heavy)
  concrete (normal, lightweight)
  brickwork
Modern materials ( light)
  sprays: Perlite-cement, Vermiculite, glass- or mineral fibre-cement sprays
  fire boards: fibro-silicate, gypsum, vermiculite
  mineral fibre or other mat materials
  intumescent coatings

## Slide 13: Steel temperature development
 Protected steelwork
a,t = · t - (e/10 -1) · g,t
with  = dp · Ap/V
p · Ap/V (g,t - a,t)
dp · ca · a ( 1+ /3)
Ap/V section factor for steel members with fire protection material [1/m]
Ap area of fire protection material per unit length [m2]
V volume of per unit length [m3]
ca specific heat of steel, from [J/kgK]
cp specific heat of the protection material [J/kgK]
dp thickness of the fire protection material [m]
t time interval [  30s ]
a,t steel temperature at time t
g,t ambient gas temperature at time t
g,t increase of the ambient gas temperature during t
p thermal conductivity of the fire protection material [W/mK]
a density of steel [kg/m3]
p density of the fire protection material [kg/m3]
cp · p
ca · a

## Slide 14: Section factor Ap/V
 Ap/V for protected steel members
Contour encase-
ment of uniform
thickness
Hollow en-
casement
of uniform
thickness
Contour encase-
ment of uniform
thickness, exposed
to fire on three sides
steel perimeter
steel cross-section area
2·(b+h)
steel cross-section area
steel perimeter - b
steel cross-section area
Ap
V
=
Ap
V
=
Ap
V
=

## Slide 15: Steel temperature
time [min]
temperature [°C]
ISO 834

## Slide 16: Structural steel
Stress-strain relationship

## Slide 17: Critical steel temperature
crit a = f (utilisation factor 0)
a,cr = 39.19 ln[1/(0.967403,833) - 1] + 482
critical temperature [°C]
utilisation factor 0

## Slide 18: Steel temperature
time [min]
temperature [°C]
a,cr
ISO 834

## Slide 19: Protected steel construction
Box protection with fire boards

## Slide 20: Protected steel beam
Intumescent coating
Before fire exposure
After fire exposure
(35 min ISO-curve)

## Slide 21: Intumescent coating
Fire resistance
thickness
fire resistance
A/V = 200
A/V = 291
variation
A/V
d = thickness of intumescent coating

## Slide 22: Protected steel construction
Composite steel and concrete structure

## Slide 23: Composite cross-sections
Columns
Beams

## Slide 24: Protected steelwork
Water cooled structure

## Slide 25: Protected steelwork
Main columns with water tank